## Sheet2
Ministry of Energy and Water Resources
Somali Electricity Recovery Project
Project Implementation Unit (PIU)
PRE-BID CONFERENCE
RFB NAME: | Design, Supply, Installation, Testing, and Commissioning of 3.5MWp Solar PV Power Plant with 7 MWh of Battery Energy Storage System for the Galkayo Electricity Company (GECO) Galkayo, Galmudug State, Somalia
RFB No. | SO-MOEWR-459178-CW-RFB
ITEM NO. | BID REFERENCE | ITEM DESCRIPTIONS | CLARIFICATION SOUGHT BY THE BIDDER | RESPONSE FROM THE EMPLOYER
1 | Volume I: Bidding Procedure and Contract Forms Bidder Qualification Section III - Evaluation and Qualification Criteria 4.2(b) Specific Experience | (b) For the above or other contracts executed during the period stipulated in 4.2(a) above, a minimum experience in the following key activities: Design, supply, installation, testing and commissioning of megawatt-scale hybrid PV plants 3.5MWp DC Solar PV 7MWhr BESS in Africa with associated substation and evacuation systems of a minimum 11kV rated system. | Evaluation and Qualification Criteria of the bid document, specifically for the condition requiring experience with a 3.5 MWp Solar PV Plant and 7MWh BESS. Geco bid '- The Bidder proposes allowing under-construction hybrid PV and BESS projects, up to the 11 kV MV system, to be considered as valid references. '- The Bidder also requests allowing projects from anywhere in the world instead of restricting eligibility to the Africa region. | - The requisite experience of the similar projects of 3No. Shall remian as indicated in the bid and should have been completed six( 6) months before the submissionn date of the bid. The whole idea is to get competent contractor with past similar experience.
- The required similar completed projects can be referenced to any where in the globe not necessarily in a frica.
2 | Volume I: Bidding Procedure and Contract Forms Commercial PCC 30. Limitation of Liability PCC 30.1 (b) | PCC 30.1 (b) The multiplier of the Contract Price is: 110% | - Bidder proposes limiting the LOL to a maximum of 100%, aligning with standard market practices for renewable energy projects. | - Employer tried to be fair in terms of apportioning the risks. Looking at the nature of the project, 110% LOL looks reasonable and fair amount. Therefore, the LOL of 110% remains as is in the bid.
3 |  |  | How many W minimum is desired to be used as panel power? If there is no limitation, can we plan it? | No limitations on the Wattage of the PV panel. However, for proper use and utilization of the space, the employer recommends the use panels/modules of higher rating subject to the client approval
4 |  |  | Can you confirm that water tank, wire fence, entrance gate, guard shack, CCTV system and lighting system will be provided by the EMPLOYER? | Refer to the Civil & structural works section in the employer's requirement for more clarity on the scope of the builders work. However, take note on the amendments as shown below.
- Water harvesting and storage tanks, plant area lighting shall be provided by the contractor
- Perimmeter fence , perimeter lighting, guard house, office building for the employer's staff, latrines and rest rooms are to be given by the local Electricity Service Provider
- CCTV to be used in securing the projects materials shall be provided by the contractor since site security is solely on the contractor's scope
5 |  |  | Can detail information be given for the administrative building (in m²)? | - This shall be designed in coordination with the contractor at the execution stage
6 |  |  | Will the panel carrier systems be aluminum? | Yes provided it is hot dipped galvanized and in line with the provided specifications in the bid document
7 |  |  | Will the operation, maintenance and repair belong to the CONTRACTOR? | Operational and maintenance of the plant shall be handled by the local Electricity Sevice Provider. However, for repair works - anything arising out of the project related defects then contractor has to undertake in line with the defect liability based on the terms given in the contract. Things to do with the functional guarantee and plant performance, contract clearly stipulates on how to handle it.
8 |  |  | Will aggregate paving be done all over the site? Or should it be only under the panels? | Overall site preparation and back filling is to be undertaken by the Electricity Service Provider. However for any builders work necessary for the erection of the power plant other than specified in the scope of the ESP shall be handled by the contractor
9 |  |  | How many times a year will panel cleaning be done and whose scope will it be? | Cleaning is part of the preventive maintenance which shall be undertaken by the local Electricity service provider not on the scope of the contractor.
10 |  |  | Is there an origin requirement for products? Can Chinese products be used? | Yes there is an origin declaration form to be filled for eligibility and compliance grounds. Employer has no preference in terms of products to be used provided the relevant specifications can be adhered to
11 |  |  | Is there a BOQ or similar document? | Refer to the price schedules provided in volume one of the bid document for pricing purposes
12 |  |  | Is there a breakdown table for quotation? | Refer to the price schedules provided in volume one of the bid document for pricing purposes
13 |  |  | Is there a spare material list? | Refer to the price schedules and to the employers requirement
14 |  |  | Proposed area/land for PV (length x width). | Refere to the provided coordinates in the bid
15 |  |  | PV Plant Setting Out Plan (if available) | Employer shall hand over a green field area with basic infrastructures to be done by the ESP. Contractor is suppose to undertake the power plant setting out plan since its the contractor's scope to do both design and the build.
16 |  |  | Any detail RFQ/report available for these SLDs mentioning PV Capacities (kWp), Battery Capacity (kwh), Inverters . | Refer to the SLD enclosed in the bid document
17 |  |  | Timeline for project construction/completion. | Refer to the SPN enclosed in bid document and the proposed PCC of the contract
18 |  |  | If any telecommunications equipment is required in hybrid PV+BESS | Refer to the SCADA & EMS section of the bid and the requisite network back bone that will enable the system to function proper. All telecom infrastructure necessary for proper function of the remote monitoring and control of the power plant shall be provided by the contractor.
19 |  |  | Is SCADA required for remote 33/11kV or just RTU? | RTU can be used in the distribution substation provided that it is linked up with the master station of SCADA in the main power plant
20 |  |  | Are the provided SLDs intended solely for reference, or are we required to proceed with the same design? | Provided SLDs are suppose to guide the contractor in coming up with its detailed design. It sets the basis for the employer's minimum requirement.
21 |  |  | Can the proof of cash flow be based on the audited report for the year 2023? Can the 2024 data be omitted? If 2024 data is required, can unaudited financial statements be used? Our financial data for both 2023 and 2024 fully meet the requirements, but the audit for the 2024 financial data has not been completed yet. | On matters of cash flow, the bidder shall demonstrate its access or availability of liquid assests, cash at hand or line of credit facility from the bank as a proof of the cash flow requirement.
22 |  |  | Is it necessary to provide supporting documents for the minimum average annual turnover, or is it sufficient to fill in the data? The tender document does not explicitly require the submission of supporting documentation. It only mentions the basis for the calculation. | - The turn over data shall be generated from audited certified financial statements of the company. Since its an extract, the two shall match and be an accurate reflection of the data provided in the financial statements
23 |  |  | Can we propose tracking installation system rather than normal installation frame? | The mounting Structures shall be the fixed -Tilt type , tracking type isn't permitted
24 |  |  | Is it acceptable to use the Turnkey central inverter solution rather than string inverters solution? | The use of central Inverter isn't permitted. Only String inverter is allowed for the project provided the speicifed rating capacity can be met.
25 |  |  | When the grid power off, how to work the mini grid? | The system shall integrated with thermal sources of Power mainly Diesel Generators which will power the grid when the PV+BESS is no longer sufficient or able to power the grid
26 |  |  | Does Bid Securing Declaration form have to give from our Bank or by the bidder itself. | Bid Securing Declaration form to be filled by the bidder as clearly stipulated and shown in the form itself
27 |  |  | Can you elaborate on payment terms? | Refer to the Appendix 1 ,section X - contract forms on terms of payment and Procedures of payment for further clarity on the payment terms. Bidders can also appraise themselves on matters of payment in the contract under clause 12.
28 |  |  | Is it acceptable to reference an on-grid project bigger than 10MW but without BESS? | The element of BESS shall be shown as part of the experience in the submitted completed project
29 |  |  | Would you please clarify if you need any simulations for the PV Power Plant? | It can be provided as a complimentary document submission to the design
30 |  |  | You just mentioned that the FIN 3.2 Average Turnover must be from 10 Years - That is on the table, the turnover stated will be from 2013 - 2023? or is it from 2016-2023 which is the 8 years. | Average turn over shall be for five years from 2019-2023. Refer to the addendum issued for the same
31 |  |  | Kindly Provide Manufacturer’s Warranty Format | Bidders shall get this from the manufacturers provided that they adhere to the specified terms and conditions
32 |  |  | Statement of adherence to technical specification format | Bidders shall provide this statement
33 |  |  | Statement of deviations and exceptions to the provisions of the Technical Specification format. | Bidders shall provide this statement
34 | Section VIII - General Conditions of Contract C. Payment 14. Taxes and Duties | "14.2 Notwithstanding GCC Sub-Clause 14.1 above, the Employer shall bear and promptly pay (a) all customs and import duties for the Plant specified in Price Schedule No. 1; and (b) other domestic taxes such as, sales tax and value added tax (VAT) on the Plant specified in Price Schedules No. 1 and No. 2 and that is to be incorporated into the Facilities, and on the finished goods, imposed by the law of the country where the Site is located." | Kindly provide information on whether it's possible to apply for tax exemptions through the World Bank for a project/investment/program. Specifically, we would like to know the process and the types of of taxes that are generally eligible for Tax Exemptions | Take note the project isn't Tax exempted. Refer to GCC 14 and its amendments in PCC 14.2 (a) & (b). Contractor shall pay all obligatory Taxes, duties, levies and any other form of tax both for the project and any other services rendered by the contractor
35 | VOLUME II. EMPLOYER REQUIREMENTS | There is no applicable trade terms for this project | Please confirm if the trade terms are FOB, DDP, or another Incotenns® 2020 standard. | The project is fully Delivered duty paid to the final destination which is the location of the Power Plant in Galkayo, Somalia