## Sheet2
Ministry of Energy and Water Resources
SOMALI ELECTRICITY SECTOR RECOVERY PROJECT
Project Implementation Unit (PIU)
PRE-BID CONFERENCE
RFB NAME: | Design, Supply, Installation, Testing, and Commissioning of 6MWp Solar PV Power Plant with 10 MWh of Battery Energy Storage System for Wamo Energy Service Company (WESCO), Kismayo City, Somalia.
RFB No. | SO-MOEWR-459175-CW-RFB
ITEM NO. | BID REFERENCE | ITEM DESCRIPTIONS | CLARIFICATION SOUGHT BY THE BIDDER | RESPONSE FROM THE EMPLOYER
1 |  |  | Firstly, the requirement for a bid bond or guarantee has not been explicitly mentioned. Could you please clarify whether a bid bond is required and, if so, what are the specific requirements regarding its amount and validity period? | Refer to BDS ITB 20.1 and 20.3 for the same
2 |  |  | Secondly, the tender documents do not provide specific details on the payment terms. It would be helpful if you could provide information on the payment method, payment schedule, and the proportion of any advance payment that may be applicable. | Refer to Appenidx 1 on Terms and Procedures of payments in Volume 1
3 | In Volume I: Bidding Procedures and Contract Forms, it is mentioned that, in the case of a Joint Venture (JV), all members are jointly and severally liable for executing the contract. However, we did not find any references or guidelines related to the Consortium formations or Channel Partner agreements. |  | Whether bids can be submitted under a Consortium or Channel Partner arrangement? | Refer to the ITB 4.1, 4.6 and section III under evalauation and qualification section. JVs are always between partners which all members shall be jointly and severally liable for the execution of the entire Contract in accordance with the Contract terms.
4 |  |  | If yes, what supporting documents are required for such submissions? | Refer to the ITB 4.1, 4.6 and section III under evalauation and qualification section. JVs are always between partners which all members shall be jointly and severally liable for the execution of the entire Contract in accordance with the Contract terms.
5 |  |  | Are there any specific forms or templates to be completed in these cases? | Refer to the ITB 4.1, 4.6 and section III under evalauation and qualification section. JVs are always between partners which all members shall be jointly and severally liable for the execution of the entire Contract in accordance with the Contract terms.
6 | The bid documents request financial statements for the last five years (2020–2024) to evaluate the bidder’s financial standing and long-term profitability. |  | What if one or more JV partners were incorporated only in 2022? They may not have five years of financial records but do meet the technical qualification criteria. Would it be acceptable to submit the available financial documents covering their active operational years? | Stick to the requirement as stipulated under 3.1 of financial capabilities in section III of the bid
7 | It is stated that the minimum average annual turnover must come from the Solar Energy Sector and must be at least USD 10 million. | In the case of a Joint Venture: - Each member must meet at least 30% of this requirement. - At least one member must meet 70% of the requirement. | If one of the three JV partners is not from the Solar sector (e.g., from construction), would it still be acceptable for them to show their turnover from their respective industry to meet the requirement? | Attentions of the bidders are drawn to 4.1 under section III ( Evlaution & Qulaification criteria) where the experience in Energy Sector Projects under contracts in the role of contractor or, subcontractor for at least the last 10 years starting 1st January 2015 is required
8 | Missing Forms in Section IV |  | Lastly, we noticed that the Forced Labour Declaration and Forced Labour Performance Declaration forms mentioned in the documents are missing from Section IV – Bidding Forms. Could you kindly provide these forms or confirm if they will be issued in a corrigendum? | The forms shall be shared in due course
9 |  | our turnover specifically in solar EPC projects is limited, though we possess technical knowledge and past experience in solar-related works. In order to comply fully with the solar-specific requirements of the RFB, we intend to participate as a joint venture with a specialized solar EPC contractor who fulfills the necessary solar project experience and technical criteria. | In this context, we kindly request your consideration to dilute or revise the turnover requirement under Clause 3.2, allowing it to reflect experience in the broader energy sector, rather than being restricted exclusively to solar. This would permit capable, financially sound companies like ours to contribute meaningfully to the project through strategic partnerships, while ensuring that the technical requirements are fully met by our JV partner | Stick requirement of clause 3.2
10 |  |  | Request for clarification on the plot boundary map to determine the layout of the photovoltaic power station and sub-distribution equipment; request for site photos, ground elevation map, and estimation of the amount of ground clearing and leveling; and confirmation of the availability of a geotechnical report for the site, considering the foundation structure of the buildings. | Plot boundary details is shared. Same for Geotechnical report. Check the employer's website
11 |  |  | Clarification on the technical specification for the energy storage system, which states an annual availability of 95%, while the commercial bid specifies 98%. Which one should be followed? | 98% annual availability as indicated in the functional guarantee requirement
12 |  |  | Confirmation whether the requirement for the energy storage container to weigh less than 30 tons is mandatory. | Same or less than 30 tonnes for the 2.0MWh system
13 |  |  | Clarification on whether the rainwater collection system, including a 10,000-liter water tank and a 5,000-liter water tank, is within the scope of the contract. | Bidder shall cater for all its water needs for the project
14 |  |  | Clarification on whether the output line engineering is within the scope of this tender. If so, please specify the type, path, and length of the power supply line. | Its not in the scope of the current bid.
15 |  |  | Confirmation whether two air conditioners for the duty room are within the scope of this tender. | All air ventilation, Acs and mechanical works are all for the contractor to undertake
16 |  |  | Can you confirm that water tank, wire fence, entrance gate, guard shack, CCTV system and lighting system will be provided by the EMPLOYER? | Refer to the Civil & structural works section in the employer's requirement for more clarity on the scope of the builders work. However, take note on the amendments as shown below.
- Water harvesting and storage tanks, plant area lighting shall be provided by the contractor
- Perimmeter fence , perimeter lighting, guard house, office building for the employer's staff, latrines and rest rooms are to be given by the local Electricity Service Provider
- CCTV to be used in securing the projects materials shall be provided by the contractor since site security is solely on the contractor's scope
17 |  |  | Can detail information be given for the administrative building (in m²)? | - This shall be designed in coordination with the contractor at the execution stage
18 |  |  | Is there a BOQ or similar document? | Refer to the price schedules provided in volume one of the bid document for pricing purposes
19 |  | Item No. 2 in 3.1.1 Solar PV Power Plant General Scope VOLUME II. EMPLOYER’S REQUIREMENTS | GPS co-ordinates are taking us inside the city area (center of Kismayo city). Please confirm the GPS co-ordinates for correct location of Solar PV plant. | Kindly refer to the attached Site lay out for more clarity
20 |  | Item No. 10 in d) GTP FOR INVERTER TRANSFORMER; APPENDIX 3: GUARANTEED TECHNICAL PARTICULARS VOLUME II. EMPLOYER’S REQUIREMENTS | Transformer vector group is mentioned as DY 11 and in the SLD it is mentioned as Dy11y11. Please confirm. | Its DY11
21 |  | 3.1.2 Solar PV Power Plant - Scope of Supply and Installations VOLUME II. EMPLOYER’S REQUIREMENTS | Is the scope includes the substation?? Please confirm. | The scope ends at the 11kV Combiner MV panel, since the existing evacuation line shall be connected to this panel
22 |  | APPENDIX 3: GUARANTEED TECHNICAL PARTICULARS VOLUME II. EMPLOYER’S REQUIREMENTS | GTP for Cables 3 core 185mm2 is missing in the tender document please provide the same. | its not in the scope of the current bid.
23 |  | g) GTP FOR THE 3C 70mm2 AL/XLPE/STA/PVC 11kV(12kV) MULTI CORE CABLE APPENDIX 3: GUARANTEED TECHNICAL PARTICULARS VOLUME II. EMPLOYER’S REQUIREMENTS | In the GTP of 70mm2 cable, current carrying capacity of cable, in air is 275 and in Duct is 219, which is not possible in Aluminium. Please clarify. | If you can't provide such cable with requisite current carrying capacity, then bidder shall propose a bigger size that can provide the required current carrying capacity or more.
24 |  | VOLUME II. EMPLOYER’S REQUIREMENTS | Please provide the Grid SLD beyond the interconnection point to have more clarity on the design and system studies. | This shall be availed later at the execution stageby the beneficiary. However, bidder is highly encouraged to make its own site visit to study the system on their own.
25 |  | VOLUME II. EMPLOYER’S REQUIREMENTS | Please provide the Upper stream SLD beyond the interconnection point to have more clarity on the design and system studies. | This shall be availed later at the execution stageby the beneficiary. However, bidder is highly encouraged to make its own site visit to study the system on their own.
26 |  | VOLUME II. EMPLOYER’S REQUIREMENTS SLD provided you. | Please clarify the input from thermal sources at the project site. Is it DG set ?? Kindly provide details. | Its all of DG. Details shall be availed at the execution stage. However, bidder shall do their own due dilligence by organizing site visits to study the systems
27 |  | 4.9.3 Technical Specification of Battery Energy Storage System and 4.9.5 Peak Management (PM) VOLUME II. EMPLOYER’S REQUIREMENTS | Rate of discharge shown in the GTP is 0.5 C, however, in section 4.9.5 Peak Management (PM) (check below screenshots) , it is mentioned that " the Contractor shall consider 4 hours of discharge during the post-solar hours". Which says rate of discharge will be 0.25 C. Please confirm. | The discharge rate is as low as 0.25 C and as high as 0.5 C
28 |  | VOLUME II. EMPLOYER’S REQUIREMENTS | The transformers are of 3150 kVA. Please confirm are these capacities fixed or we can provide transformers with additional capacity. | Capacity isn't fixed but bidder shall be mindful about redundancy. If the provided Transformers in the SLD shown to be 2No. Then regardless of the higher capacity than the 3150KVA, the proposed shall remain two for redundancy puproses.
29 |  | VOLUME II. EMPLOYER’S REQUIREMENTS | Please provide us the approximate land area or land boundary file of the Solar PV project site. | Refer to the provided site lay out
30 |  | RFB-Vol-I-Bidding-Procedure-and-Contract-Forms-WESCO-Kismayo C. Preparation of Bids | Does the scope include the substation? If so, kindly provide the transmission line SLD and the grid substation SLD, including details of the planned and incoming bays. | This scope doesn’t include the evacuation line but is included up to the combiner level. Referred Bays in this case are the incomer and the outgoer bays at the combiner level
|  | VOLUME II. EMPLOYER’S REQUIREMENTS 9.0 LIGHTNING & EARTHING PROTECTION SYSTEM | Kindly provide the geo-technical report | See attached report
31
32 |  | e) GIS Synchronization/ Combiner Panel APPENDIX 3: GUARANTEED TECHNICAL PARTICULARS VOLUME II. EMPLOYER’S REQUIREMENTS | In the SLD shared by you, there is no bus coupler. However, in the GTP FOR 11 kV GIS SYNCHRONIZING/ COMBINER PANEL, there is requirement of a bus coupler is mentioned. Please clarify. | Bus coupler shall be provided in the panel
33 |  | e) GIS Synchronization/ Combiner Panel APPENDIX 3: GUARANTEED TECHNICAL PARTICULARS VOLUME II. EMPLOYER’S REQUIREMENTS | In the GTP FOR 11 kV GIS SYNCHRONIZING/ COMBINER PANEL, in Item no. 22, it is mentioned 33kV cable compartment (however, the Solar PV project is at 11kV) and nominal current rating is 2000 ampere. Please confirm both points. | Its an error in the GTP. Its supposed to be 11kV and the nominal current is 1250A.
34 |  | 4.9.9 BESS Transformer VOLUME II. EMPLOYER’S REQUIREMENTS | It is mentioned that the "BESS Transformer may be dry type or Oil type as per specifications provided elsewhere in this document". However, nowhere only Inverter Transformer technical specifictaion are provided. Please provide details on this. | Specification remain but for PCS ( bi-directional) transformers. Bidder shall submit the proposed PCS Transformer specification enclosed in the bid
35 |  | 3.1.2 Solar PV Power Plant - Scope of Supply and Installations VOLUME II. EMPLOYER’S REQUIREMENTS | In oint number 6 ist mentioned that, "Synchronization of the Existing 11kV HT Switchgear Panels including Vacuum or SF6 Circuit Breakers, Current Transformers, Voltage Transformers, Relays and other accessories at the inverter stations". Is there existing Switgear panels? If yes, please share the technical documents such as SLD. | Details shall be availed at the execution stage. However, bidder shall do their own due dilligence by organizing site visits to study the systems
36 | 3.1.1 Solar PV Power Plant General Scope | Acceptable PR ratio for the PV is 90%" a PR of 90% is unrealistically high for typical PV systems . Industry benchmarks generally recommends 83% PR due to factors like target inverter efficiency.system losses, environmental conditions, and | Kindly confirm of PR requirement can be revised to 83% or provide technical justification for the 90% | Acceptable PR ratio for the project is 85%
37 | i) GTPs: SOLAR PV MODULES | Front glass coating is 2: 3.2mm anti reflect coating, | Please clarify that such a PV module is a single glass module, whether you can choose a double glass module. | Bifacial double glass( front and rear) Modules are acceptable in the bid
38 | 3.1.2 Solar PV Power Plant - Scope of Supply and Installations | Solar PV modules which shall be of monocrystalline, necessary Mounting Module Structures (MMS), all necessary Aluminium for both MMS and PV modules reinforced concrete foundations (ground mount modules) olts, nuts and all interconnection necessary for modules. | Is the MMS required to be Anodized Aluminium? Is aluminum, zinc and magnesium plating OK? | Only hot dipped galavnized Aluminium or steel are is acceptable as they offer better corrosion protection
39 | VOLUME II. EMPLOYER REQUIREMENTS 4.1.2 WARRANTIES FOR MODULES |  | What is the wind resistance requirement of Mounting Module Structures (MMS) | Bidder is supposed to find out this data on their own since its instrumental in the detail design
40 | VOLUME II. EMPLOYER REQUIREMENTS 4.1.2 WARRANTIES FOR MODULES | The PV modules power generated degradation shall not exceed 0.5% per annum or guaranteed performance of 90% after 25 years of service. The modules shall be warranted for minimum of 10 years against all material/ manufacturing defects and workmanship." | Kindly confirm acceptance of 87.5% post-25-year performance and 12-year warranty as per industry norms. If the original terms are mandatory, please specify approved module brands/models meeting these criteria | Stick to the requirement. Employer isn't obliged to provide or suggest any brand names.
41 | Please provide the coordinate positions of the boundary points of the photovoltaic power station. |  | The tender document only provides the coordinate position of the project location. We need more coordinate positions to determine the scope of the photovoltaic power station. - | See attached lay out
42 |  |  | please confirm whether purchasing of the document is a prerequisite for bid dsubmission. | Bid document is free downloadable from employer's webiste for free, no charges to be paid.
43 |  |  | The required material for the mounting module structure (MMS) is hot dip galvanized steel or Aluminum? | Both are acceptable as long as are of hot dipped galvanized with required strenght
44 |  |  | For MMS, kindly confirm whether ramming pile can be considered an acceptable alternative to a concrete foundation. | Concrete foundation is a must
45 |  |  | For DC Cable in RFP Page 28, the dc cable cannot be armoured from manufacture and this cables can be fitted in conduit, did you accept the normal cable used for Solar with CU/TUV/XLPE???? | provided its enclosed or contained in a conduit
46 |  |  | The transformer requested for PCU is copper, does this specs applied to PCS transformer also???? | All are supposed to be of copper winding
47 |  |  | “Inverter transformer” (section 4.6 of Vol 2) shall be considered for the required specs and not “power transformer” (section 5 of Vol 2), please confirm. | is for inverter Transformers
48 |  |  | For the inverter transformer, Kindly confirm that a neutral bushing solely for testing purposes shall not be considered mandatory, unless explicitly required by the equipment manufacturer. The transformer neutral bushing is mentioned in section 4.6.3 of Vol 2. | Confirmed
49 |  |  | The maximum ambient temperature before electrical equipment derating is 40°C or 45°C? | Its 45ᵒ C
50 |  |  | Could You please provide an Autocad drawing for the site area, if available. | Find the attached PDF version of the site lay out
51 |  |  | Could You please share actual pictures of the sites, if available. | Refer to the attached provide site lay out
52 |  |  | Is it acceptable to use PV modules with integrated 4mm2 cables instead of 6mm2? Since 4mm2 is the market standard. | Stick to the requirement
53 |  |  | For the 11KV Combiner panel for evacuation, could You please provide a clearer SLD for the combiner panel since the provided one in page 2 of the SLD file is not clear for pricing. | See revised SLD
54 |  |  | The 11kV combiner panel building is to be constructed by the bidder? | Its is in the scope of the bidder
55 |  |  | 100mm layer of ballast aggregates under solar field platform (section 11.1 of Vol 2) along with removal of 200mm of top soil (section 11.18 of Vol 2) fall under the employer responsibility, Please confirm. | its in the scope of the bidder
56 |  |  | Water harvesting into a total of 15000 liters tank is required along with the needed purification? | Yes
57 |  |  | The following statement is unclear: "For exposed outdoor installations, cables shall be laid in covered cable trenches, plastic or steel ducts, depending on the available space." Can DC and AC cables be routed on a cable tray fixed to the ground instead? | Stick to the requirement
58 |  |  | In the equipments material the life time of plant is 30 years and for batteries storage is 20 years while in the general the life time of plant is 40 years | General life time of the plant is for 40 years.
59 |  |  | The requested inverter is required to have an LED screen. While available inverters on the market can be monitored via phone or desktop, allowing visibility of all parameters, on-site monitoring only displays fault alarm lights and operational status. Please confirm if this meets the requirements | Acceptable
60 |  |  | Grid Code of the plant if available | Shall be shared at the execution stage
61 |  |  | The type of plant ? The the uperstream network MVA? | Question not clear.
62 |  |  | For Panels linear performance in the general specs we request that he should 90% after 25 Years while in GTP is 88% after 25 years | Stick to the requirement
63 |  |  | Outdoor fire extinguishers are typically regulated by NFPA 10, the International Fire Code (IFC), and OSHA standards?? | Shall be compliant of all
64 |  |  | After the harvesting tank is full, where should the excess water go? | 'Bidder shall cater for all its water needs for the project
65 |  |  | For panel cleaning, only valves near the MMS tables are used. What is the maximum required distance between them? | Not in the bidder's scope
66 |  |  | Taxes on panels, inverters,structure and electrical equipments? | Refer to the PCC clause 14.2 (a) & (b)
67 |  |  | For GTP for BESS the rated power is 1016 witch is 0.5c for each container 2.032MWp however in the requested rated power is 2.5MW for hole system that is mean 0.25C | Refer to the response given under question 27
68 |  |  | The performance ratio requested is imposible based on tilt angle and cost effective so 85% can be reachable, did you accept this value?? | Acceptable
69 |  |  | The breaker has been requested as withdrawable, while it is also specified to be of GIS type. However, in GIS systems, breakers are typically non-withdrawable. Please clarify whether you require a withdrawable AIS breaker or a non-withdrawable GIS breaker. | Stick to the requirement
70 |  |  | The location specified in the tender is not clear; it appears to be on the roof of a building in Kissmayo. | Refer to the lay out issued