## Sheet1
Ministry of Energy and Water Resources
Somali Electricity Recovery Project
Project Implementation Unit (PIU)
PRE-BID CONFERENCE HEALTH & EDUCATION FACILITIES-PUNTLAND STATE OF SOMALIA HELD ON 12TH FEBRUARY, 2026
ITEM NO. | BID REFERENCE | ITEM DESCRIPTIONS | RESPONSE FROM PIU/MINISTRY
1 | PV Installation Type (Rooftop or Ground-Mounted) | The tender documents do not specify whether the PV systems will be installed on rooftops or on the ground.If rooftop installation is intended, could you please confirm the roof type (reinforced concrete, steel structure, sandwich panel, etc.)?In the case of concrete roofs, is mechanical anchoring by drilling permitted, or is the use of a ballast mounting system mandatory? | Different facilities have different types of system mounting requirement- Some are of Ground mount while others are of Roof type. It’s the contractor's duty to determine in their survey and design on the required mode of system mounting for the system PVs and methods of installing and anchorage of the same either on the ground or on top of the roof.
2 | Generator Integration for Hospital Facilities | Considering these are education& health projects, we assume existing generators are present on-site. Therefore, we request clarification on the following:
|  | In the event the batteries are fully depleted, should the system automatically activate the existing generator? | Yes. Interfacing with the existing electrical sources is a must.
|  | Alternatively, will the generators be decommissioned or disconnected as part of the hybrid system implementation? | Refer above.
|  | If the generator must remain operational, an ATS (Automatic Transfer Switch) and related cabling, panels, and labor will be required, representing additional cost. Should this be included in our proposal? | Its supposed to be quoted by the bidder in its costing.
3 | MPPT Input Requirements | The tender documents do not specify required MPPT input criteria.Can the number and configuration of MPPT inputs be selected freely by the contractor according to the system design? Or is there a minimum technical requirement that must be met? | Contractor has the liberty to design the system and submit for approval by the employer.
4 | Potential Cost Implications Following Site Survey | According to the tender, the awarded contractor must perform site surveys for all facilities to confirm design-critical parameters.Given this obligation: There may be technical conditions discovered during site surveys that could increase the final project cost. Is there a mechanism to address such concern (e.g., pre-participation survey or exact location coordinates to investigate the sites further)? | Refer to ITB 7.4 of the BDS where the same site visit has been highly encouraged to be undertaken by the bidder at the bidding stage. Bidder can have its own internal plan and arrangement to make such visits. In case additional issues arise during execution, bidder has no right to put in any sort of claim as the opportunity is still there ( now at the bidding stage) to verify the site related data before tender closure.
5 | Load Type, Critical Loads, and Load Profile | The tender documents do not specify the detailed load profile or the nature of the connected loads. We kindly request clarification on the following points:
|  | Do the stated loads refer exclusively to critical loads, or do they represent the total facility load, including non-critical circuits in the event of a blackout? | The provided PV and BESS capacity are to cater the required total energy consumption demand of the respective facilities. For respective hourly demand, the contractor shall provide and capture in its design which shall be done during project execution stage.
|  | Is there any significant inductive load expected in the system such as AC units, ventilation fans, or other motor-driven equipment? | Inductive loads are hugely present which are mainly due to the nature of inductiveness of some equipment. Bidder shall allow the proposed inverter to be able to work with PF ranges from 0.8-0.95 or even to unity
|  | This information is essential for accurate inverter sizing, surge load considerations, and battery autonomy calculations. | See above responses
6 | Taxation, VAT, and Possible Exemptions | We were unable to find any references to taxation, VAT, exemptions, or anti-dumping measures within the tender documents. For proper financial planning, we kindly request clarification on the following: Will there be any tax exemptions, VAT relief, or anti-dumping exemptions applicable to PV and BESS equipment for this project? | Refer to clause 14.2 (a) & (b) of the contract PCC where Various duties, levies and Taxes from both the federal or state levels shall be borne by the contractor.
7 | Form of submission (ITB 22.1) | Considering the delivery challenges and extended delivery times experienced with courier services like DHL Express and TNT, could we explore the possibility of submitting bids electronically to ensure efficiency and timeliness? | No electronic submissions are accepted. The Ministry shall not take the responsibility of any bids submitted through courier services such as DHL. Only bids submitted physically to the Ministry's offices shall be considered for evaluations.
8 | Financial Bid Opening (ITB 26.6) | Given that electronic bid submission is not permitted and financial envelopes are not password-protected, how will the security of financial bids be handled, preventing any premature opening. In the interest of transparency and adhering to best practices, we kindly request that the total bid amount for all submissions be disclosed during the public bid opening. Thanks for your kind consideration in this regard. | The bid is based on the two envelope bidding process which doesn't allow any opening of the financial envelopes during the 1st bid opening stage where only technical bid shall be opened. The security provided is that all financial bids shall be isolated during the 1st opening, put in separate container/box,sealed off, signed and initialled by all the bidders' attendees. When the financial bids for the contractors who proceeded to the second round (financial stages )are to be opened, all the initial provisioned security measured shall be considered and checked. After all, financial bid opening shall occur in the presence of the contractors who have succeedeed to proceed to next stage which is the financial bid. Separate USB for the Technical Bids and the Financial Bid and included in their separate envelopes.
10 | N/A | Certain Facilities have a grid connection and backup DG sets in certain cases. Grid supply at these facilities is available for approx 24 hrs/day. Our understanding is that solar systems to be supplied are OFF GRID. Pls confirm that no connecivity is required to the electrical grid or to the backup DG Generators? | Solar PV and BESS are supposed to be the primary source of power for these facilities. Grid Connection and that of DG shall serve as back up. The proposed system shall take into account the integration of these various system. Hence Hybrid mechanism required shall support multiple source of power
9 | N/A | At locations where nonfunctional solar installations are installed. Are we authorized to remove and replace these systems? | No. since the existing solar fcailities are outside of this current project scope
10 | N/A | At locations where the target capacity cannot be installed due to insufficient exposed area or roof space, the installed capacity can be reduced. | Stick to the requirement. The designed minimum capacity shall be achieved.
11 | N/A | The availability of electricity from the grid at the facilities is good. We propose and seek your concurrence to supply hybrid rather than OFF-GRID PV systems. | The system is hybrid capable of integrating multiple source of power
12 | Mounting structure requirements | Please state if there are any preferences by the end-users regarding the mounting of the PV panels (roof mounted/ground mounted) for the different sites. The consideration can also be made based on the structural strength of the building rooftop. | No preference but depends on site conditions. Successful contractor shall do due dilligence in finding out what is best for the site.
13 | Building plans | Please share any structural drawings of the buildings. | Some of these building have been built decades ago, no structural drawings are available. It is therefore highly recommended for bidders to arrange voluntary random site visits to appraise themselves with the reality on the ground.
14 | Containerized solution | Please confirm if containerized solution incorporating the hybrid inverters and the batteries can be offered. | Allowed as per specifications
15 | N/A | Alternately, please confirm if there is adequate space inside the facilities to install the required inverters, batteries and electrical distribution and protection systems. | Spaces are available. However, it is contractor's obligation to make ground related due dilligence and confirmation on what works for their proposed systems
16 | Technical rooms | Please confirm if there is adequate space within the facilities or premises to install the required hybrid inverters, batteries and electrical distribution and protection systems. | Spaces are available. However, it is contractor's obligation to make ground related due dilligence and confirmation on what works for their proposed systems
17 | Location of existing main distribution boards | Please provide the location of the existing main distribution boards (or distance from container to MDB) so the cables connecting the new distribution board to the existing distribution board can be sized and routed. | Most facilities don't have unified standarized main /sub main distribution systems. Mostly don't have properly manufactured/fabricated switchboards with the required protection. It is this sole reason that in this current bid scope, there is provision for all these mishaps to be addressed and standarized to offer the required switching/isolation and protection. Therefore, bidders are highly urged to make voluntary site visits to some random sites to appraise and make understanding on the ground situations which shall inform on their costing strategy.
18 | N/A | Please confirm if the proposed inverters (for all 3 types of buildings, are required to turn on/off the diesel generator in case of unavailability of PV power) | Priority shall be for ESS first then after ESS is about to deplete then inverter shall trigger an external Auto-change over to switch on the Generator Set.
19 | AC-Coupled system | Are DC-Coupled solution acceptable as they are more cost and energy efficient than AC-coupled solution, and DC-coupled solutions involve fewer energy transition stages | Both options are allowed either DC-AC or DC-DC coupling
20 | Container Location | The bid requires a containerized solution as per the below statement found on page 160. Can you please specify the location of the container in each site. Control room containerized solution for all indoor equipment including BESS, Inverters, Air Conditioning, IT devices etc. | Containerized solutions are required. Locations shall be proposed by the successful bidder and submit as part of the shop drawings for approval/
21 | Internal rewiring | As the scope of “internal rewiring” is vague, and as there are 23 sites, we appreciate if this can be quoted separately (as OPTIONAL) to avoid its effect on the evaluation of the bid. Alternatively, kindly specify the number of rooms in each facility so that we can estimate the amount of “internal wiring” works requested | Kindly quote as per the bid. For the Number of rooms, bidders are urged to make their own local arrangement to familiarize themselves with the ground situation.
22 | Containeraized Solution Description | Kindly confirm that the containerized solution mentioned in the tender refers to the one of the ISO containers as per below: | These shall be the purpose made type containerized solutions by the manufcaturers not this dry type shown below. Shall have all associated services such as cooling and ventilation systems. It is factory built type from manufacturers
23 | Operations and Maintenance (O&M) Costs | How does the O&M cost be factored in after the initial 1 years O&M Services. | The quoted price for the O&M services shall remain the same throughout if the contract for the services needs to be extended beyond the currently estimated 1 years.
24 |  | Under ITB 11.2 (m) of the BDS shall be modified to read as shown on the next column | Detailed design of the proposed system showing all necessary technical assumptions applied, calculations, system sizing, spare capacity, projected system losses etc. The design shall cover the major equipment/devices including Modules, Arrays, Mounting Module Structures, Combiners, Inverters, Battery Inverters, Batteries, Communication & Monitoring system, Switchgears, Protection, Earthing and Lightning Protection, Cables (both DC & AC), HVAC system and any other system required to make the plant functional. Bidders to submit electrical schematic diagram of the proposed PV systems design and configuration showing the main equipment/components and control equipment/switchgear, their interconnection, and the power flows. One diagram for EACH type of facility; General Hospital, Maternity Hospital and Health Centre.
25 |  | Is surplus power generated by the solar system allowed to be exported to the grid? | Not at all. What is not to be consumed or stored shall remain as uncaptured or an excess power not consumed
|  | Are the site loads already segregated (critical vs. non-critical) | Not needed as the the proposed system is for all connected loads
|  | Do any existing breakers or switches require replacement as part of this project? | Where its needed, contractor shall do at its own cost
|  | Please provide existing single-line diagrams (SLDs) / wiring diagrams and any additional technical specifications needed for switchgear design. | Its upon bidders to find out by undertaking voluntary site visits
|  | Does the 10 kW system also require dedicated switchgear? | All distirbution main and sub boards are in the bid scope
|  | Please confirm grid stability conditions. | Grid is stable. However, for interfacing with the PV & BESS systems, Inverters shall be able to conditioned the electrical system parameters
|  | What type of internet connectivity is available at each site? | RFID, GSM and Fiber are all available
26 | PV Module Technology
| Reference: Section VII – Employer’s Requirements → Solar PV Modules.The specification refers to Mono/Polycrystalline (Mono PERC) PV modules. | Query: Kindly confirm whether N-type (TOPCon / HJT) PV modules are also acceptable, provided all IEC compliance requirements are met. | Admissible as they are of high quality and effeciency
27 | Module Wattage Range-Reference: Section VII – Employer’s Requirements → PV System Description The minimum and maximum module wattage range is not explicitly stated. | Kindly confirm the acceptable wattage range per facility to allow optimized system design. | No specific rating required. It’s the contractor to propose the rating of the modules by being mindful on proper space utilization
28 | IEC Standards – Equivalence
| Reference: Section VII – Employer’s Requirements → Standards and Certifications PV modules are required to comply with IEC 61215 and IEC 61730. | Kindly confirm whether equivalent EN / UL certifications are acceptable with valid third-party test reports | Acceptable
29 | PID Resistance Requirement
| Reference: Section VII – Employer’s Requirements → PV Module Performance & Reliability (Page ~174) IEC 62804 (PID resistance) is mentioned. | Kindly clarify whether PID test report is mandatory at bid stage, or if manufacturer declaration is acceptable. | Its about comppliance. No submission required at the bid stage for the same.
30 | Corrosion Protection
| Reference: Section VII – Employer’s Requirements → Structural Materials Hot-dip galvanized steel structures are specified. | Kindly confirm the minimum zinc coating thickness (µm) required. | minimum required is 100 µm
31 | Warranty – Performance Degradation
| Reference: Section VII – Employer’s Requirements → Warranties .The performance warranty mentions 90% output at 25 years. | Kindly confirm whether a standard 80% output at 25 years warranty is acceptable if supported by manufacturer certification | Stick to the required 88% for the 25 years period.
32 | Inverter Warranty | .
| Reference: Section VII – Employer’s Requirements → Inverters The inverter warranty period is not clearly defined. | Kindly confirm the minimum inverter warranty duration required. | Refer to the respective GTP sheet for the same. Its 10 years.
33 | Module Traceability (RFID)
| Reference: Section VII – Employer’s Requirements → Traceability & Identification RFID tagging of PV modules is specified. | Kindly confirm whether QR-code based digital traceability is acceptable as an alternative. | Acceptable
34 | Internal Wiring Scope
| Reference: Section VII – Employer’s Requirements → Electrical Works / Internal Distribution (Page ~181)Some facilities may require internal wiring rehabilitation. | Kindly confirm whether wiring layouts and quantities will be provided, or if this scope shall be assessed and included by the Contractor. | Its in the contractor's scope to do the assessment, design, procurement and installation for the same
35 | Existing Generator & Grid Interface
| Reference: Section VII – Employer’s Requirements → Existing Electrical Infrastructure / Power Sources | Please confirm the availability of diesel generator(s) at each project site. | Its case by case. Some have, others not
|  | If generator(s) are available, kindly provide details of the existing Grid–Generator interconnection, including how seamless power supply is currently achieved. | Its contractor to find out finer details before bid submissions
|  | i) Is any Automatic Transfer Switch (ATS) or manual changeover switch available? | Its contractor to find out finer details before bid submissions
|  | ii) Please provide Grid incomer breaker details, including breaker type, rating, and grid supply parameters. | Its contractor to find out finer details before bid submissions
|  | iii) Please provide Generator incomer breaker details, including generator rating, make, model, and controller details, if available. | Its contractor to find out finer details before bid submissions
|  | iv) If generator is not available, kindly confirm whether future DG provision / connection point is required to be included in the bidder’s scope. | It’s a must
36 | System Operating Logic (Grid–Solar–Battery–DG)
| Reference: Section VII – Employer’s Requirements → System Control Philosophy / Energy Management | 1.1 Kindly confirm the system operating logic, specifically:
|  | i) Are batteries allowed to charge from the grid during night time or periods of no solar irradiance? | Its strictly from PV side only.
ii) When grid is available:
|  | Should non-critical loads always be powered from grid? | All connected loads shall be powered from the Grid
|  | If there is no solar irradiance and battery SOC is low, shall critical loads be powered from grid? | All connected laods shall be powered from the Grid
|  | During grid outage, shall battery / solar power supply only critical loads | All connected laods shall be powered from PV/BESS Systems
|  | iii) Please confirm the system operating logic when generator is available, including generator priority and interaction with battery charging. | 1st priority is the PV, then surplus energy goes to BESS during solar hours. After non solar hours or when the solar radiance starts to fade, BESS takes over, followed by Grid and lastly the DG
37 | Fencing Requirement for Ground-Mounted Systems
| Reference: Section VII – Employer’s Requirements → Civil & Site Security Works | Please confirm whether fencing is required for ground-mounted solar PV systems. | Its required
|  | If fencing is required, kindly provide technical requirements (type, height, access gates). | Its upon contractor to make the proposal
|  | If not specified, kindly confirm whether bidder may design fencing based on standard design practice. | Its upon contractor to make the proposal
38 | Existing Wiring Diagrams & Design Inputs
| Reference: Section VII – Employer’s Requirements → Electrical Design & Switchgear | Kindly provide existing wiring diagrams / single line diagrams (SLDs) and additional electrical specifications required for switchgear design and integration. | Its contractor to get such details from the site at the bid stage
39 | BESS (Battery Charging from grid )
| Section VII → System Operation / Energy Management / BESS Operation | Please confirm whether battery charging from grid is permitted during night time or periods of no solar irradiance.If permitted, kindly confirm whether it is time-based, SOC-based, or unrestricted. | Not allowed
40 | Battery Charging from Generator
| Reference:Section VII → Integration with Existing Power Sources / Generator Interface | Please confirm whether battery charging from generator is permitted when generator is available, and the corresponding operating logic. | Not allowed
41 | Priority Logic (Solar–Battery–Grid–Generator)
| Reference:Section VII → Control Philosophy / System Logic | Please confirm the priority order among Solar, Battery, Grid, and Generator for:
|  | l Load supply | Load supply then surplus goes to BESS for storage
l Battery charging
42 | BESS Testing & Acceptance Criteria
| Reference:Section VII → Testing & Commissioning | Please confirm whether battery capacity test, load test, and performance demonstration are mandatory during commissioning, and the acceptance criteria | Perform all necessary functional tests.
43 | BESS Battery Disposal & Recycling
| Reference: Section VII → Environmental & O&M Responsibilities | Please confirm responsibility for end-of-life battery disposal / recycling and whether it is included under O&M scope. | Not in the current scope
44 | BESS Future Battery Expansion Provision
| Section VII → Future Expansion / Design Margin | Please confirm whether future battery capacity augmentation is envisaged and whether space and electrical provisions are required. | BESS are supposed to be modular type. For future Augmentation are currently not in the current scope
| Section VII → Warranties & Guarantees | Please confirm the battery warranty basis:
l Calendar years
|  | l Cycles / throughput | Cycles
|  | l End-of-warranty SOH (%) | 70%
45 | BESS Thermal Runaway Protection
| Reference: Section VII → BESS Safety & Protection | Please confirm whether thermal runaway detection and mitigation is required at cell, module, or rack level. | Required at all levels
46 | BESS Fire Detection & Suppression
| Section VII → Safety, Fire Protection & Compliance | Please confirm whether fire detection and fire suppression systems are mandatory for battery rooms / containers, and the applicable standard | Its required
47 | Minimum Battery SOC Reserve
| Section VII → BESS Performance Requirements | Please confirm the minimum SOC reserve (%) to be maintained during normal operation and during grid outage. | 5-10%
48 | Battery Autonomy Definition
Reference:
| Section VII → BESS Sizing / Autonomy Requirements | Please clarify whether the specified battery autonomy is based on Average critical load, or Maximum critical load. | Is based on maximum peak loading
49 | Degree of Protection (IP Rating)
Reference:
| Section VII → Environmental Conditions / Enclosures | Please confirm minimum IP rating for:Indoor panels Outdoor panels | IP31 for indoor and IP65 for outdoor
50 | Metering & Instrumentation Scope
Reference:
| Section VII → Metering & Monitoring | Please confirm whether energy meters, multifunction meters, and power quality meters are required at: | Only at the Incomer levels
|  | Also confirm communication protocol (RS-485 / Ethernet). | RS-485, Ethernet, GIS Sim card, RFID, RS 232 etc are required for relevant system interface
51 | Spare Ways & Future Expansion
Reference:
| Section VII → Future Expansion / Design Margin | Please confirm the percentage Main panelsof spare feeders / ways to be provided in:Main panels & DBs | Refer to the price schedule requirement and the O&M Segment
52 | O&M & Spares
Reference:
| Section VII → O&M Requirements | Please confirm mandatory spares for breakers, relays, meters, and the required quantities. | Refer to the price schedule requirement and the O&M Segment
53 | Soil Resistivity Data
Reference:
| Section VII → Site Data / Civil Works | Please confirm whether soil resistivity test reports are available for all sites.If not available, kindly confirm whether bidder shall assume standard soil resistivity values for earthing design. | Its in the bidder's scope
54 | Earth Resistance
Reference:
| Section VII – Employer’s Requirements → Earthing & Grounding System (≈ Page 188–192) | The specification appears to indicate an earth resistance value of 0.5 Ohms. Kindly confirm:
|  | Whether 0.5 Ohms is mandatory for all sites, or | Yes, its mandatory
|  | Whether ≤ 1.0 Ohm is acceptable where soil conditions do not permit achieving 0.5 Ohms without excessive civil works. | Soil shall be treated to achieve the requisite values
|  | Whether the requirement applies to overall earth grid resistance or individual earth pits. | Separate stand alone earth pits
|  | Whether augmentation measures (additional pits / chemical earthing) are expected to be included to achieve 0.5 Ohms. | required for achieveing the set values
55 |  | Please confirm whether all sites have existing technical rooms with adequate ventilation and sufficient heat dissipation capacity for LT panel installation. | Some facilities have, others not. Its in the contrcator's scope to do an assessment and provide a proper Main Distirbution Board with all requisite ventilation and cooling services.
56 |  | Please confirm whether all sites are equipped with existing diesel generators, Grid if any site have Transformers or LT panels?. | Not all have utitlity connection or diesel generators but a good number of them do have.
57 |  | If yes, kindly provide generator ratings (kVA/kW) for each site or by site category. | It’s the contractor to find out such details in their own voluntary site visits
58 |  | If grid and generator not available future extension provision for grid and generator required also specify the no of sites that doestnt have grid and generator. | It’s the contractor to find out such details in their own voluntary site visits
59 |  | Please confirm if any site has existing PV system and its operational status. Does it need to integrate with new solar system? | Some sites have an existing PV systems and their integration is a must
60 |  | Please share if possible Site images or documents of sites- wiring plan, Civil Drawings. | It’s the contractor to find out such details in their own voluntary site visits
61 |  | Since the Systems sizes are smaller, does it really need SCADA? Because Price Schedule is included with SCADA, We propose instead of SCADA, EMS remote monitoring for this system size | Remote monitoring is needed through web based systems
62 |  | Please provide the location or distance of the existing main distribution boards to technical room, Distribution boards (or distance from container to MDB) and distance between technical room solar system to connection point. | It’s the contractor to find out such details in their own voluntary site visits
63 |  | Evaluation of Technical Part – Design, supply & Installation: detailed design procedure, supply and installation processes on the PV power plant, Substation, evacuation line and associated equipment. | Evacuation to load centers within the facilities is what is within the scope of the project not to external fcailities
64 |  | The system size is very small, We hope substation and evacuation is not part of the scope, kindly clarify.
65 |  | Please confirm Existing ATS or change availability and its size | It’s the contractor to find out such details in their own voluntary site visits
66 |  | Please provide load profile for all sites | Work with the provided capacity in the bid
67 |  | Please confirm whether roof strengthening, if required after site visit, is under Employer’s scope or Contractor’s scope. | In contractor's scope
68 |  | Please confirm whether roof access (ladder / staircase / hatch) is available at all sites, If roof access is not available, please confirm whether provision of roof access is under Employer’s scope or Contractor’s scope. | In contractor's scope
69 |  | Please confirm whether permanent roof safety systems such as guard rails, walkways, lifelines, anchor points, and fall protection systems are required, If required, please confirm whether these safety systems are under Employer’s scope or Contractor’s scope. | In contractor's scope
70 |  | Kindly confirm whether, at sites where an Electrical Control Room with sufficient space is available, the same may be utilized for installation of Battery Energy Storage System (BESS). | Subject for employer's approval. For bigger facilities, BESS shall be in their own IP rated containers
71 |  | Please confirm whether module cleaning system is under Employer’s scope or Contractor’s scope. | In the contractor's scope. Refer to the O&M strategy enclosed in the bid
72 |  | Please confirm whether building permits / local authority approvals are under Employer or Contractor scope. | In contractor's scope
73 |  | Please confirm availability of internet / GSM / fiber connectivity at sites for monitoring systems, If not available, please confirm whether providing SIM cards, routers, or communication infrastructure is under Employer or Contractor scope. | In contractor's scope
74 |  | Please confirm maximum allowable noise levels for equipment | As per the recommendation of each equipment by the relevant standards
75 |  | Please confirm whether ventilation / HVAC is required for inverter and battery rooms and scope responsibility | Refer to the employer's requirement. All are needed for.
76 |  | Please confirm whether customs clearance, duties, and local taxes are under Employer or Contractor scope. | In contractor's scope
77 |  | We request you to please inform us the name of the Port having Container handling facilities in the Puntland State where we shall send our goods. | Contractor shall find out such information on their own
78 |  | Ref Section-X – Contract Forms for Payment Terms : Please clarify how the mode of payment will be made ? | Refer to Appendix 1 of terms and procedures of payment as enclosed in the bid
79 |  | Please clarify whether the Employer will establish an Irrevocable Confirmed Letter of Credit from a First Class European Bank having corresponding Bank in India. | Employer isn't obliged to do so. See appendix 1 of the proposed payment modality.
80 |  | Ref Schedule No. 1 Payment Terms : Please clarify that within how many days after the Delivery of goods at Site after Certified and Approved will be issued for release of the second 40% Payment. | Within 45 days of getting an invoice from the contractor
81 |  | Please clarify whether the issuance of Certificate and Approval for goods would be carried out at all the 35 different Sites/Hospitals/Health Facilities, or this would be carried at any central warehouse ? | Shall be done through an inspection of goods in their respective warehosues
82 |  | Please clarify that how much time will be taken by the Employer to issue us the “Completion Certificate” and “Operational Acceptance Certificate” respectively. | read relevant clauses under GCC 24 & 25 for the same as its clearly detailed and shown.
83 |  | Where the goods need to be delivered ? Will it be required to be delivered at any central warehouse or at all 35 different installation locations ? | To different facilities for installations
84 |  | Since some buildings have flat roof and some sloping roof, please furnish us the details of the building Roof tops with sizes available for mounting the Solar PV Modules and the details of Roof top structure (for the sloping roof) to enable us work out whether the roof tops are capable of installation of the Solar PV Modules. | Bidders are highly urged for a site visit before quoting and later after the award for assessment to find out such details
85 |  | In Sr. No. 4.2 (a) – ‘Specific Experience’ it is mentioned that the requirement for Experience is Solar PV System Hybrid of 100 kWp with Battery Storage; and also requires PV System Hybrid of 10 kWp and above with battery storage. This is confusing and therefore, please clarify that if the bidder has Specific Experience of 100 kWp PV system hybrid with battery storage , then why again this requirement of 10 kWp System ? | Bid requires to show of having relevant sepcific experience for at least two projects one with a capacity of 100kWp and the other one 10kWp. It could be of more in capacity but not less than the stated capacity
86 |  | Then in Sr. No. 4.2.(b) – ‘Specific Experience’ it is mentioned that the requirement of at least 2 solar PV plants over last 5 years with PV capacity of 100 kWp and above. This is followed up with all others above 10 kWp. At least 2 of the Projects shall have incorporated BESS. These requirements are confusing and we request you to please clarify categorically what is your requirement ? | See above response under 85
87 |  | 1.1 In Sr. No. 4.2 (c) – Specific Experience in managing ES aspect : Please note and appreciate that all the Solar PV systems would be installed on all the Existing 35 buildings and moreover, such installations does not require any environmental safety aspects and does not violate any environmental issues. Therefore, we request you to please reconsider this and delete this requirement. | It’s the bid requirement and still stands.
88 |  | Please clarify that for the BESS system if the BESS Vendor/manufacturer furnishes Warranty for the BESS, then why again the Warranty statement is separately required for the Batteries | Please comply with the bid requirement
89 |  | Please furnish the total Connected Load of all the 35 buildings where the PV System would be installed. Please appreciate this would enable us to design the PV System properly. | Work with the provided capacity in the bid
90 |  | EXTENSION OF DEADLINE FOR BID SUBMISSION : In order to prepare our comprehensive and compertitive bid, we sincerely request you to please extend the Bid Submission Date till 11th April, 2026. | Unfortunately, we are unable to grant any extension. The closing date remains as shown in the bid